# Parameter List

| Function | F_ | Function Description | Unit | Range | Factory setting | Page | Note |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0 | Factory Adjustment |  |  | 0 | 24 |  |
| Accel. Time Decel. Time | 1 | Accel. time | 0.1Sec | 0.1 ~ 999 S | 5.0 | 24 | *1 *3 |
|  | 2 | Decel. time | 0.1Sec | 0.1 ~ 999 S | 5.0 | 24 | *1 *3 |
| Operation mode | 3 | 0: Forward / Stop, Reverse / Stop 1:Run/Stop, Forward / Reverse | 1 | 0 ~ 1 | 0 | 25 |  |
| Motor rotation direction | 4 | 0: Forward 1: Reverse | 1 | 0 ~ 1 | 0 | 25 | *1 |
| V/F Pattern | 5 | V/F pattern setting | 1 | 1 ~ 6 | 1/4 | 26 | *2 |
| Frequency upper/lower limit | 6 | Frequency upper limit | 0.1Hz | 1.0 ~ 120Hz (1~200)*4 | 50/60Hz | 27 | *2 *3 |
|  | 7 | Frequency lower limit | 0.1Hz | - ~ 120Hz (1~200)*4 | 0.0Hz | 27 | *3 |
| SPI frequency | 8 | SP1 frequency | 0.1Hz | 1.0 ~ 120Hz (1~200)*4 | 10Hz | 27 | *3 |
| JOG frequency | 9 | JOG frequency | 0.1Hz | 1.0 ~ 10.0Hz (1~200)*4 | 6Hz | 27 |  |
| Start / Stop Control | 10 | 0: Keypad 1: Terminal (TM2) | 1 | 0 ~ 1 | 0 | 27 |  |
| Frequency Control | 11 | 0: Keypad 1: Terminal (0~10v / 0~20mA) 2: Terminal (4~20mA) | 1 | 0 ~ 2 | 0 | 28 |  |
| Carrier frequency control | 12 | Carrier Frequency Setting | 1 | 1 ~ 5 (1~10)*4 | 5 | 28 |  |
| Torque compensation | 13 | Torque compensation gain | 0.1% | 0.0 ~ 10.0% | 0.0% | 28 | *1 |
| Stop method | 14 | 0:controlled deceleration stop 1:free run to stop | 1 | 0 ~ 1 | 0 | 29 |  |
| DC braking setting | 15 | DC braking time | 0.1S | 0.0 ~ 25.5S | 0.5S | 29 |  |
|  | 16 | DC braking injection frequency | 0.1Hz | 1 ~ 10Hz | 1.5Hz | 29 |  |
|  | 17 | DC braking level | 0.1% | 0.0 ~ 20.0% | 8.0% | 29 |  |
| Electronic thermal Overload protection | 18 | Protection base on motor rated current | 1% | 50 ~ 100% (0~200)*4 | 100% | 30 |  |
| Multifunction input connection point | 19 | Multifunction input terminal 1 (SP1) function | 1: Jog 2: Sp1 3: Emergency stop 4: External Base Block 5: Reset 6: SP2*4 |  | 2 | 31 |  |
|  | 20 | Multifunction input terminal 2 (RESET) function |  |  | 5 | 31 |  |
| Multi-function output | 21 | Multifunction output terminal | 1: Operating 2: Frequency reached 3: Fault |  | 3 | 32 |  |
| Function | F_ | Function Description | Unit | Range | Factory setting | Page | Note |
| Reverse Lock-Out | 22 | 0: REV run 1: REV run Lock-Out | 1 | 0 ~ 1 | 0 | 32 |  |
| Momentary power loss | 23 | 0: enabled 1: disabled | 1 | 0 ~ 1 | 0 | 33 |  |
| Auto restart | 24 | Number of Auto-restart times | 1 | 0 ~ 5 | 0 | 33 |  |
| Factory setting | 25 | 010: Constants initialization to 50Hz system 020: Constants initialization to 60Hz system |  |  |  | 34 | *2 |
| SP2 frequency | 26 | SP2 frequency | 0.1Hz | 1.0~200Hz | 20 | 34 | *4 |
| SP3 frequency | 27 | SP3 frequency | 0.1Hz | 1.0~200Hz | 30 | 34 | *4 |
| Direct start | 28 | 0:enable 1:disable | 1 | 0 ~ 1 | 1 | 34 | *5 |
| Software version | 29 | CPU program version |  |  |  | 35 |  |
| Fault Log | 30 | Fault log for three faults. |  |  |  | 35 |  |

NOTE:

*1: Indicate this parameter can be adjusted during running mode.

*2: Please refer to F_25.

*3: If the setting range is above 100, the setting unit becomes 1.

*4: New function for CPU version V1.9 and above.

*5: New function for CPU version V2.1 and above

# Parameter function description

F_00 Factory adjustment parameter. Do not change.

F_01 : Acceleration time = 0.1 ~ 999 sec F_02 : Deceleration time = 0.1 ~ 999 sec

- Acceleration / Deceleration time calculation formula:

| Accelerate time = F_01 x | Setting Frequency |
| --- | --- |
|  | 60 Hz |

| Decelerate time = F_02 x | Setting Frequency |
| --- | --- |
|  | 60Hz |

Hz

Time

F_01

F_02

F_03: Operation mode selection = 0: Forward / Stop, Reverse / Stop 1: Run / Stop, Forward / Reverse

NOTE 1: F_03 takes effect only when F_10 = 1 (external operation control)

F_03 = 0 control

method

3 FWD /Stop

5 COM

F_03 = 1 control method

3 Run / Stop

4 REV /Stop

4 FWD/ REV

5 COM

ON

TM2 PIN3

ON

TM2 PIN4

Forward

F_03=0

Output

Reverse

F_03=1

Output

Forward

Reverse

Note: Reverse command is ignored when F_22 = 1

F_04: Motor rotation direction setting = 0: Forward 1: Reverse

Although there is no Forward / Reverse push button on the digital control panel, it is possible to adjust forward / reverse function by changing the F_04 setting.

NOTE:

When F_22 =1: Reverse is disabled, the F_04 cannot be set to 1.

The keypad indication would display “LOC”.

F_05: V/F pattern setting = 1 ~ 6

Selecting F_05 = 1-6 to select one of the six preset V/F patterns. (Refer to the following tables)

| Specification | 50 Hz System 100 B C |  |  |
| --- | --- | --- | --- |
| Application | General Application | High starting torque | Decreasing torque |
| F_5 | 1 | 2 | 3 |
| V (%) V (%) V (%) 100 B C 100 B C 1 2.5 50 120 1 25 50 120 1 2.5 50 120 Hz Hz Hz V/F pattern |  |  |  |
| Specification | ##### 60Hz System |  |  |
| Application | General Application | High starting torque | Decreasing torque |
| F_5 | 4 100 B C | 5 100 B C | 6 |
| V (%) V (%) V (%) 100 B C 1 3.0 60 120 1 3.0 60 120 1 30 60 120 Hz Hz Hz V/F pattern |  |  |  |

| F_5 | B | C |
| --- | --- | --- |
| 1/4 | 10% | 8% |
| 2/5 | 15% | 10.5% |
| 3/6 | 25% | 7.7% |

F_06: frequency upper limit range=1~120Hz F_07: frequency lower limit range=1~120Hz (1~200Hz with CPU versionv1.9 and above)

F_06: Factory setting refers to F_25.

F_07 (freq. Lower limit)

Internal frequency signal

F_06 (freq. Upper limit)

(NOTE)

Frequency setting signal

NOTE:

If F_07 = 0 Hz, 	The frequency instruction is equal to 0Hz, the inverter will

stop at 0 speed.

If F_07 > 0 Hz, 	The frequency instruction F_07, the inverter will

output a minimum speed according to the setting in F_07

F_08: SP1 frequency = 1 ~ 120Hz(1~200Hz:CPU version v1.9 and above) F_09: JOG frequency = 1 ~ 120Hz(1~200Hz:CPU version v1.9 and above)

1.	When F_19 or F_20 = 2 and the multifunction input terminal is ON, the inverter operates at sp1 frequency (F_08)

2.	When F_19 or F_20 = 1 and the multifunction input terminal is ON, the inverter operate at jog frequency (F_09)

3.	The priority of reading frequency setting is: Jog→ Sp1→Keypad setting or external frequency signal using a speed pot.

F_10: Start / Stop Control = 0: Keypad = 1: Terminal (TM2)

NOTE: When F_10=1 (Terminal Control), emergency stop on the Keypad is enabled.

When F_10=1, please refer to the descriptions of F_23/24, in order to avoid the damage to the human and the machine.

### Hz

Time

F_10=1

or =0

F_09=10Hz

F_19=1

ON

OFF

OFF

OFF

F_08=30Hz

F_20=2

ON

OFF

ON

OFF

ON

OFF

F_11: Speed Control = 0: Keypad = 1: Analog Speed Pot Terminal (TM2) (0 ~ 10V / 0-20mA) = 2: Analog Speed Pot Terminal (TM2) ( 4-20mA )

NOTE 1:

When jog frequency or Sp1 frequency is

F_06

switched on, the frequency is setup by Sp1

speed, the ▲▼ buttons on the keypad is

F_11=1

disabled.

Original setting will be restored after the Sp1

connection is removed.

F_11=2

NOTE2:

0mA

0V

4mAAAAA

20mA

10V

During the contact closure of the jog function,

the keypad control remains in a sleep state until

the jog contact connection is re-opened.

F_12: Carrier Frequency = 1 ~ 10

| F_12 | Carrier frequency | F_12 | Carrier frequency | F_12 | Carrier frequency |
| --- | --- | --- | --- | --- | --- |
| 1 | 4 kHz | 5 | 8 kHz | 9 | 15 kHz*1 |
| 2 | 5 kHz | 6 | 10 kHz*1 | 10 | 16 kHz*1 |
| 3 | 6 kHz | 7 | 12 kHz*1 |  |  |
| 4 | 7.2 kHz | 8 | 14.4 kHz*1 |  |  |

NOTE: *1: Available for CPU version V1.9 and above.

2: If F_12=7~10, the inverter must operator with low load.

Although an IGBT TYPE inverter can provide a low audible noise level during its operation, it is possible that the switching of the high carrier frequency may interfere with external electronic components (or other controllers) or even cause vibration in the motor. Adjusting the carrier frequency can usually correct this problem.

F_13: Torque compensation gain = 0 ~ 10 %

To enhance Inverter output torque patterns according to the B, C voltage points on the V/F pattern (refer to F_05 description) and the (F_13) for this feature.

Voltage

100%

B

F_13=

C

Hz

1

2.5/3.0

50/60

NOTE: When F_13 = 0, the torque boost function is disabled.

F_14 Stopping method = 0 : Controlled deceleration stop = 1 : free run to stop F_15 DC braking time = 0 ~ 25.5 sec F_16 DC braking starting frequency = 1 ~ 10 Hz F_17 DC braking level = 0 ~ 20 %

If F_14 = 0

When the inverter receives the stop command, it decelerate to the pre-set frequency setup by F_16 after this the output voltage level that is set in the F_17; will determine the amount of DC voltage that’s injected into the motor.  The time duration to perform this stopping function is setup in F_15.

Run Command

Output Frequent

Deceleration Time

DC Braking Frequency

DC Braking Time

If F_14 = 1

The inverter stops output immediately after receiving the stop command. The motor will enter into a free running state until it comes to a complete stop.

F_18: Motor rated current = 50~100 %(0~200%: CPU version v1.9 and above)

### 1.	The electronic thermal overload protection for motor:

(1)	Motor rated current = Inverter rated current x F_18

- F_18 = Motor rated current / inverter rated current

- When the load is within 100% of the motors rated current, the operation continues. When the load reaches 150% of the motors rated current the operation is allowed to continue for 1 minute. (Refer to curve (1) in Figure 3)

- After protecting the motor with the electronic thermal switch activated, the inverter is cut off immediately. The OLI light will flash. To resume operation, push the RESET button or activate an external reset connection wired to terminal 2.

- When the motor is operating at low speeds, the heat dissipation efficiency is lower. The electronic thermal activation level is also reduced. (to change from curve (1) to curve (2) in Figure 3. Choose the appropriate F_05 setting according to the applied motor to reach the desired performance.

### 2.	The electronic thermal protecting for inverter:

(1)	When the load is within 103% of the inverters rated current, the operation continues. When the load reaches 150% of rated current of the inverter, the operation will continue for 1 minute. (Refer to curve (1) of figure 3)

(2)     After the activation of the electronic thermal switch,  the inverter is shut off immediately. The OL2 light will flash. To resume the operation, push RESET button or activate an external reset contact on terminal 2.

F_05 = 4,5,6

60 Hz standard motors

10090

60

F_05 = 1,2,3

50 Hz standard motors

Minute

%

Decay

10090

60

Decay

- 50

(Figure 1)

20        60

100       150

(Figure 3)

In Percentage of Current

(Figure 2)

1.0

%

% of current

F_19: Multifunctional input terminal 1 function = 1~ 5(1~6:CPU version v1.9 and above) F_20: Multifunctional input terminal 2 function = 1~ 5(1~6:CPU version v1.9 and above)

### 1.	F_19=1 or F_20 =1: JOG control (refer to F_09)

2.	F_19, F_20 =2 or 6 Multi-speed control:

### F_19=2  & F_20=6:

| TM2 SP1 Terminal | TM2 RESET Terminal | Output frequency |
| --- | --- | --- |
| ON | OFF | F_08 |
| OFF | ON | F_26 |
| ON | ON | F_27 |

F_19=6 ﹠F_20=2:

| TM2 SP1 Terminal | TM2 RESET Terminal | Output frequency |
| --- | --- | --- |
| ON | OFF | F_26 |
| OFF | ON | F_08 |
| ON | ON | F_27 |

NOTE: F_19,F_20=2 or 6 are new function for CPU version v1.9 and above.

### 3.	F_19, F_20 =3: External emergency stop

- When the external emergency stop signal is activated, the inverter proceeds to decelerate and stop, (ignoring the setting of F_14). The inverters E.S. light will flash after stopping. After the emergency stop signal is deactivated, turn the RUN switch OFF and then ON again to cycle it. (F_10 =1) Or, push the RUN key (F_10=0). The inverter will then resume operation and restart. If the emergency stop signal is removed before the inverter stops, the inverter will still execute the emergency stop.

### 4.	F_19, F_20 =4: External Base Block (Immediate Shut Down)

- When the external base block signal is activated, the inverter output will be immediately shut off (ignoring the setting of F_14) and flash b.b. Light.  After the base block signal is deactivated, turn the RUN switch OFF and then ON again (F_10 = 1) or push the RUN key (F_10=0), the inverter will restart from the original starting frequency.

Time

Run/Stop                                  on                                off  on

F_19=3                              off                          on

F_02

Hz

Time

Run/Stop                                    on                                       off         on

F_20=4                          off                             on

### F_19, F_20 = 5: Auto Reset when inverter faults.

F_21: Multi-function output terminal control = 1 ~ 3

### 1.	F_21 = 1: Run mode signal

### 2.	F_22 = 2: At Frequency Speed Signal

### 3.	F_21 = 3: Fault signal

Terminal1 and2 of TM2 are activated at CPF, OL1, OL2, OCS, OCA, OCC, Ocd , Ocb , OVC , LVC , OHC.

Hz

Time

F_21=1

Terminal 1 & 2          on

F_21=2

Terminal 1 & 2                                          on

F_22: Reverse Lock-Out = 0: REV command = 1: REV command Lock-out

NOTE:

When F_04 is set to 1 (reverse), F_22 cannot be set to 1, in order to properly lockout

a motors direction, F_04 must be set at 0 before setting F_22 to 1.

F_23: Auto-restart after momentary power loss =0: auto-restart enabled =1: auto-restart disabled

1.	When the AC power supply is temporary below low voltage protection levels because of power company issues or encountering large current loading in the same power supply system, the inverter will stop its output immediately. If the power source resumes within 2 seconds, the inverter can restart by using its speed search program.

2.	When F_23=0:

(1) If the momentary power loss is less than 2 seconds, the inverter resume operation automatically via speed search at 0.5 seconds after power up.  The number of auto-restart times is not limited by F_24.

(2) If the momentary power loss is long, the operation of the inverter is based on the setup of F_10 and the condition of external switch.

(3) If the time of momentary loss is between the above two, whether the inverter will auto-restart depends on F_24:

F_24=0: auto-restart disabled.

F_24=1~5: auto-restart enabled 1~5 times.

3. When F_23=1,

(1) Power up after momentary power loss, the inverter will not start. Even under F_24>0.

(2) If the momentary power loss is long, the inverter must be restart manually. The operation of the inverter is based on the setup of F_10 and the condition of external switch.

4.  When restart the inverter, the operation of the inverter is based on the setup of F_10 and the condition of external switches (FWD/REV button).

(1) When F_10=0, the inverter will not start after restart.

(2) When F_10=1 and the external switch (FWD/REV button) is OFF, the inverter will not start after restart.

(3) When F_10=1 and the external switch (FWD/REV button) is ON, the inverter will start automatically after restart.  Attention: Base on safety reason, please turn off the external switch (FWD/REV button) after power loss to avoid possible damage to the machine and the human body after sudden regeneration of power.

F_24: Number of Auto-restart times = 0~5

1.	When F_24=0, the inverter will not auto-restart after a malfunction break away from operation.  (Except for momentary power loss, please refer to F_23 for details)

2. When F_24=1~5: the inverter will resume operation via speed search at 0.5 second under auto-restart after malfunction break away. (Except for momentary power loss, please refer to F_23 for details).

3.	When the inverter is set to deceleration or DC breaking, the transient restart procedure is not performed.

4.	If either of following situations should develop, the auto restart times will be reset:

- No additional malfunction (in operation or stop) occurs within 10 minutes.

- Press RESET button.

F_25: Return to Factory Pre-Settings = 010: Constants initialization to 50Hz system = 020: Constants initialization to 60Hz system

1.	When F_25 is set to 010, all parameters are restored to factory settings. The settings of F_05 =1 and F_06 = 50. F_25 is restored back to 000 after the reset process is complete. (50Hz operation)

2. When F_25 is set to 020, all parameters are restored to factory settings. The settings of F_05 =4 and F_06 = 60. F_25 is restored back to 000 after the reset process is complete. (60Hz operation)

F_26: SP2(1~200Hz) , Multi-speed2 (Reference to F_19 ﹠F_20)

F_27: SP3(1~200Hz) , Multi-speed3 (Reference to F_19 ﹠F_20)

F_28: Direct start = 0 : Direct start enable when remote Run command on = 1 : Direct start disable when remote Run command on (CPU version V2.1 and above)

When F_28 = 1 and control mode is remote control (F_10 = 1), Inverter can not start if RUN switch is ON when power is engaged, Must be turned the RUN switch OFF and turned ON again, Then Inverter can start.

F_29: CPU program version

F_30: Last three faults

1.	Last three faults: indicate the sequence of the occurrence of malfunctions by the location of decimal point. x.xx indicates a recently happened malfunction. xx.x indicates the last malfunction that happened. xxx. Indicates the earliest malfunction in the record.

2.	After entering the F_30 function, the x.xx trip record will be displayed first. After that, press▲ button and you can read activity in a chronological order.  xx.xxxx.x.xx ,,, consecutively.

3.	After entering F_30 function, if the RESET button is pressed, the trip record will be cleared. Indication display -.--, --.-, and ---.

4.	When the content of trip indicates O.CC, it will indicate the latest trip code is OC-C and so on.

# Malfunction Indications and Countermeasures

## 1.	Manual reset inoperative malfunctions

| INDICATION | CONTENT | POSSIBLE CAUSE | COUNTERMEASURE |
| --- | --- | --- | --- |
| CPF | Program error | Outside noise interference | Place a RC surge absorber in parallel with the noise generating magnetic contact |
| EPR | EEPROM error | EEPROM defective | Replace EEPROM |
| OV | Voltage too high while not operating | 1. Power source voltage too high. 2.Detection circuitry defective | 1. Examine the power supply 2.Return the inverter for repair |
| LV | Voltage too low while not operating | 1. Power source voltage too low. 2. Detection circuitry defective. | 1. Examining the power supply 2. Return the inverter for repair |
| OH | Inverter over heat while not operating | 1. Detection circuit defective. 2. Environment over-heat or poor ventilation | 1. Return the inverter for repair 2. Improve ventilation |

## 2.	Manual reset operative malfunctions (Auto-Reset inoperative)

| INDICATION |  | CONTENT |  | POSSIBLE CAUSE |  | COUNTERMEASURE |
| --- | --- | --- | --- | --- | --- | --- |
| OC | Over-current at stop condition |  | Detection circuit malfunction |  | Return the inverter for repair |  |
| OL1 | Motor over-load |  | 1. Loading too large 2. Improper V/F model setting 3. Improper F_18 setting |  | 1. Increase capacity of motor 2. Adjust to use a proper V/F curve setting 3. Adjust F_18 according to instruction |  |
| OL2 | Inverter over-load |  | 1. Loading too large 2. Improper V/F model setting |  | 1. Increase capacity of inverter 2. Adjust to use a proper V/F curve setting |  |

## 3.Manual Reset and Auto-Reset Operative Malfunction

| INDICATION | CONTENT | POSSIBLE CAUSE | COUNTERMEASURE |
| --- | --- | --- | --- |
| OCS | Transient over-current starting machine | 1. Motor coil short-circuit with external casing 2. Motor connection wire short-circuit with grounding 3. Transistor module damaged | 1. Examining motor 2. Examining wiring 3. Replace transistor module |
|  | Over-current at acceleration OCA OCC | 1. Acceleration time setting too short 2. Improper V/F feature selection 3. Applied motor capacity exceeds inverter capacity | 1. Adjust acceleration time to longer setting 2. Adjust to a proper V/F curve 3. Replace and install another inverter with appropriate capacity |
|  | Over-current at steady speed | 1. Transient alteration of the loading 2. Transient alteration of the power supply | 1. Examining the loading configuration 2. Install inductor on the power supply input side |
| OCd | Over-current at deceleration | Deceleration setting too short | Adjust to use a longer acceleration time |
| OCb | Over-current at breaking | DC Breaking frequency, breaking voltage, or breaking time setting too long | Adjust to reduce settings of F_15, F_16, or F_17 |
| OVC | Over-voltage at operation/deceleration | 1. Deceleration time setting too short or inertial loading too large 2. Power supply voltage variation too large | 1. Adjust to use a longer deceleration time 2. Install a inductor on the power supply input side 3. Increase the capacity of inverter |
| LVC | Insufficient voltage level at operation | 1. Power supply voltage too low 2. Power supply voltage variation too large | 1. Improve power source quality 2. Adjust to use a longer acceleration time 3. Increase capacity of inverter 4. Install a reactor on the power supply input side |
| OHC | Heat-sink over heated at operation | 1. Loading too heavy 2. Ambient temperature too high or poor ventilation | 1. Examining the loading 2. Increase capacity of inverter 3. Improve ventilation |

# Special Condition Description

| INDICATION | CONTENT | DESCRIPTION |
| --- | --- | --- |
| SP0 | Zero Speed Stopping | When F_11 = 0, F_7= 0 and frequency setting < 1 Hz When F_11 = 1, F_7<(F_6/100), and frequency setting <(F_6/100) |
| SP1 | Fail to start directly | 1. If the inverter is set to external operation (F_10 = 1) and direct start is disabled (F_28 =1), the inverter cannot be started and will flash SP1 when operation switch turned to ON after applying power (see descriptions of F_28). - Direct start is possible when F_28 = 0. |
| SP2 | Keypad emergency stop | The inverter setup to external operation (F_10=1). If the STOP key in the keypad is pressed at the middle of operation, the inverter stops according the setting in F_14 and flash SP2 after stop. The RUN switch must be turned OFF than ON to restart the machine. |
| E.S. | External emergency stop | When the external emergency stop signal is activated through the multi-function input terminal, the inverter decelerates and stops. Inverter flashes E.S. after stops. (Refer to instruction for F_19 for detail). |
| b.b. | External BASE BLOCK | When the external BASE BLOCK signal is activated through the multifunction terminal, the inverter stop output immediately and flash b.b. for indication. (Refer to instruction for F_19 for detail) |

# Keypad Operation Error Instruction

| INDICATION | CONTENT | POSSIBLE CAUSE | COUNTERMEASURE |
| --- | --- | --- | --- |
| LOC | Motor direction locked | 1. Attempt to reverse direction when F_22 = 1 2. Attempt to set F_22 to 1 when F_04 = 1 | 1. Adjust F_22 to 0 2. Adjust F_04 to 0 |
| Er1 | Keypad operation error | 1. Press ▲or ▼ keys when F_11=1 or under sp1 operation 2. Attempt to modify F_29 3.Attempt to modify parameter that is not allowed to be modified during operation (refer to parameter list) | 1. Use ▲or▼keys to adjust frequency setting only after F_11=0 2. Do not modify F_29 3. Modify in stop mode |
| Er2 | Parameter setting error | 1. F_6≦F_7 | 1. F_6 > F_7 |

# General Malfunction Examination Method

| ABNORMALITY | CHECK POINT | COUNTERMEASURE |
| --- | --- | --- |
| Motor Inoperative | Is the power source voltage delivered to L1, L2 terminal (is the charging indicator illuminated)? | - Check if the power source on. - Turn power source OFF and then ON again. - Reconfirm the power voltage level. |
|  | Is there voltage output from output terminal T1, T2 and T3? | - Turn power source OFF and then ON again. |
|  | Is the motor wired correctly? | - Check motor wiring. |
|  | Is there any abnormal condition of the inverter? | - Refer to malfunction handling instructions to examine and correct wiring. |
|  | Is the forward or reverse instruction loaded? |  |
| Motor Inoperative | Is the analog frequency setting loaded? | - Check to see if wiring for analog frequency input signal is correct? |
|  | If the operation mode setting correct? | - Check if the frequency input setting voltage is correct? |
| Motor operate in opposite direction | Is wiring on the output terminals T1, T2 and T3 correct? | - Operate by digital? |
|  | Is the wiring for the forward and reverse signals correct? | - Wiring should be in accordance with the U, V, W terminals of motor. |
| Motor operation speed fixed | Is the wiring for analog frequency input correct? | - Examining the wiring and correct it. |
|  | Is the operation mode setting correct? | - Examining the wiring and correct it. |
|  | Is the loading too heavy? | - Check the Operation panel |
| Motor operation at speed too high or too low | Is the specification of motor (poles, voltage) correct? | - Reduce loading |
|  | Is the gear ratio correct? | - Reconfirm motor specification. |
|  | Is the highest output frequency setting correct? | - Reconfirm gear ratio |
|  | Is the voltage on motor side reduced extremely? | - Reconfirm highest output frequency |
| Abnormal speed variation at operation | Is the loading too heavy? | - Reduce loading variation |
|  | Is the loading variation too large? | - Increase inverter and motor capacity |
|  | Is the input power source steady and stable? | - Install AC reactor on the power supply input side |

Chapter 4:Troubleshooting Procedures

## ( Continued )

# Error handling of malfunction indication of OC.OL

# Error handling of malfunction indication of OV.LV

# (1).	Motor inoperative

# (2).	Motor over-heat

# (3).	Disturbing motor operation

## Routine examination and periodical examination

Inverter requires routine and periodical examination and maintenance

Carry out the examination only after the “ Power LED ” indicator goes off for at least 5 minutes

| Maintenance item | Maintenance description | Examination period |  | Examination method | Criterion | Countermeasure |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Routine | 1 Year |  |  |  |
| Installation site environment | Reconfirm environment temperature and humidity | ○ |  | Refer to installation instructions and measure with thermometer and hygrometer | Temperature: -10~40 OC Humidity: under 95% without condensing | Improve installation site environment |
|  | Check and remove any flammable material nearby | ○ |  | Visual inspection | No foreign object |  |
| Inverter Installation and Grounding | Is there any abnormal vibration on the installation site? | ○ |  | Visual and audio Inspection | No foreign object | Tighten loose screw |
|  | Is the grounding resistance within acceptable range? |  | ○ | Measure resistance by multi-meter | 200V class under 100 ohm | Improve grounding |
| Input power source voltage | Is the voltage of the primary circuitry normal? | ○ |  | Measure voltage by multi-meter | Voltage level conforming specification | Improve input power source |
| Inverter external terminal mounting screw | Is the tighten parts secured? |  | ○ | Visual inspection. Use screwdriver to verify screw tightness | No abnormality | Tighten loose screw or return for repair |
|  | Is there any sign of breakage on the terminal panel? |  | ○ |  |  |  |
|  | Is there any obvious rusty condition? |  | ○ |  |  |  |
| Internal wiring of inverter | Is it deformed or skewed? |  | ○ | Visual inspection | No abnormality | Replace or return for repair |
|  | Is the insulation of wire broken? |  | ○ |  |  |  |
| Heat-sink | Is it accumulating dust or dirt? | ○ |  | Visual inspection | No abnormality | Clean up dust or dirt |
| PCB | Is it accumulating conductive metal or oil stain? |  | ○ | Visual inspection | No abnormality | Clean up or replace PCB |
|  | Is there any over-heated or burnt component? |  | ○ |  |  |  |
| Cooling fan | Is there any abnormal vibration or noise? |  | ○ | Visual and audio inspection | No abnormality | Replace cooling fan |
|  | Is it accumulating dust or dirt? | ○ |  | Visual inspection |  | Clean up |
| Power component | Is it accumulating dust or dirt? |  | ○ | Visual inspection | No abnormality | Clean up |
| Capacitor | Is there any sign of strange order or leakage? | ○ |  | Visual inspection | No abnormality | Replace capacitor or inverter |
|  | Is there any sign of swelling or bulging? | ○ |  |  |  |  |

# Maintenance and Examination

Frequent examination and maintenance is not required for the inverter.

To maintain appropriate reliability, please proceed with following periodical examination. Remember to turn off power supply and wait till the Power LED goes off before proceed. (Due to the large amount of remaining charges in the internal capacitors.)

- Clean out internal dust and dirt.

- Check out mounting screws on every terminal and parts. Tighten loose screws.

- Dielectric strength test

- Remove all conducting wires between Drive and outside world. Power must be turned OFF.

- The dielectric strength test inside Drive should be carried out only for T-VERTER major circuitry. Use DC 500V: high resistance meter. Measured resistance should be higher than 100M ohm.

CAUTION: Do not perform dielectric strength test to the control circuit.

Input power source

DC-500V high-resistance meter

Grounding terminal

Motor

L1 (R)			  T1 (U)

L2 (S)	Drive	  T2 (V)

T3 (W)

Connection for dielectric strength test

# Voltage Current Measurement

The voltage and current measurement on the primary and secondary side of the inverter may be different due to instrumentation variations. Refer to following diagram for measurement:

A1

Signal-phase power supply

To motor

V1

W1

A4

A5

A6

V4

V5

V6

W3

W4

| L1 (R) L2 (S) | T1 (U) T2 (V) T3 (W) |
| --- | --- |

Different kinds of instrument

| Measurement | Measuring point | Instrument | NOTE (Measurement criterion) |
| --- | --- | --- | --- |
| V1 A1 Input voltage VI |  | Moving-iron |  |
| Input current Ii |  | Moving-iron |  |
| W1 Input power Pi |  | Power-meter | P=W1 |
| Input power factor PFi | Calculate power factor by the input voltage, input current and input power |  |  |
| V4 V5 V6 Output voltage Vo |  | Rectifier (Moving-iron not allowed) | Maximum voltage difference between wires under 3% |
| A6 A4 A5 Output Current Io |  | Moving-iron | Under the inverter rated current |
| W4 W3 Output power Po |  | Power-meter | Po=W3+W4 |
| Output power factor |  |  |  |

# EMI Filter (class B) Specification

| #### Model | Dimension (mm) | Current (A) | #### Inverter model |
| --- | --- | --- | --- |
| #### E2F-2102 | #### 156 X 76 X 25 | #### 10A | E2-2P2-M1F/E2-2P2-H1F E2-2P5-M1F/E2-2P5-H1F E2-201-M1F/E2-201-H1F |
| # E2F-2202 | #### 172 X 120.2 X 11 | #### 20A | E2-202-H1F E2-203-H1F |
| # E2F-4103 | #### 172 X 120.2 X 11 | #### 10A | E2-401-H3F E2-402-H3F E2-403-H3F |

# DIN RAIL Specification

| Model | Dimension (mm) | Inverter model |
| --- | --- | --- |
| DIN E2-201 | 130 x 72 x 7.5 | E2-1P2/1P5/101/2P2/2P5/201 E2-202/203/401/402/403 |

## Specification of Braking Resister and Input Reactor

| MODEL | Braking transistor build-in | Braking resister build-in | Torque of braking | Model of braking resister | Input AC Reactor |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Current (A) | Inductance (mH) |
| E2-2P2-x1xx | X | X | 20% | Note 1 | 3 | 7.0 |
| E2-2P5-x1xx | X | X | 20% | Note 1 | 5.2 | 4.2 |
| E2-201-x1xx | X | X | 20% | Note 1 | 9.4 | 2.1 |
| E2-202-Hxx | ○ | X | 20% | BRN2-202 | 19 | 1.1 |
| E2-203-Hxx | ○ | X | 20% | BRN2-203 | 25 | 0.71 |
| #### E2-401-H3xx | ○ | X | 20% | BRN2-401 | 2.5 | 8.4 |
| E2-402-H3xx | ○ | X | 20% | BRN2-402 | 5.0 | 4.2 |
| E2-403-H3xx | ○ | X | 20% | BRN2-403 | 7.5 | 3.6 |

○ : Built-in       X: Without built-in

Note 1: Without transistor and resister built-in.

#### Specification of Braking Resister

| Model of Inverter | Model of Braking resister | Rate of Motor (KW) | Specification of Braking Resister |  | Braking Resister ED(%) | Torque of braking (%) | Size of resister (L*W*H) mm | Size of carton (L*W*H) mm | Weight (5pc) N.W (kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | (W) | (Ω) |  |  |  |  |  |
| E2-202-Hxxx | BRN2-202 | 1.5 | 150 | 100 | 10 | 119 | 215*40*20 | 325*225*70.5 | 2.1 |
| E2-203-Hxxx | BRN2-203 | 2.2 | 200 | 70 | 9 | 116 | 165*60*30 | 200*195*80 | 3.2 |
| E2-401-H3xx | BRN2-401 | 0.75 | 60 | 750 | 8 | 125 | 115*40*20 | 200*195*80 | 1.1 |
| E2-402-H3xx | BRN2-401 | 1.5 | 150 | 400 | 10 | 119 | 215*40*20 | 325*225*70.5 | 2.1 |
| E2-403-H3xx | BRN2-403 | 2.2 | 200 | 250 | 8 | 128 | 165*60*30 | 200*195*80 | 3.2 |

Note: 1. Braking level: 385/770Vdc for E2-200/400 series

2. Braking resister mounting is below:

5cm

Inverter

P  R

TM1                                             Braking resister

#### PARAMETERS TABLE

| CUSTOMER |  |  |  |  | MODEL |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| APPLICATION |  |  |  |  | TELEPHONE |  |  |  |
| ADDRESS |  |  |  |  |  |  |  |  |
| F_## | Value Setting |  | F_## | Value Setting |  | F_## |  | Value Setting |
| F_00 |  |  | F_11 |  |  | F_22 |  |  |
| F_01 |  |  | F_12 |  |  | F_23 |  |  |
| F_02 |  |  | F_13 |  |  | F_24 |  |  |
| F_03 |  |  | F_14 |  |  | F_25 |  |  |
| F_04 |  |  | F_15 |  |  | F_26 |  |  |
| F_05 |  |  | F_16 |  |  | F_27 |  |  |
| F_06 |  |  | F_17 |  |  | F_28 |  |  |
| F_07 |  |  | F_18 |  |  | F_29 |  |  |
| F_08 |  |  | F_19 |  |  | F_30 |  |  |
| F_09 |  |  | F_20 |  |  |  |  |  |
| F_10 |  |  | F_21 |  |  |  |  |  |