# 1.	Foreword

To fully employ all functions of this AC Drive, and to ensure the safety for its users, please read through this operations manual in detail. Should you have any further questions, please feel free to contact your local distributor or regional representative.

## ※Please use Precaution with this product

The AC Drive is a power electronic device.  For safety reasons, please read carefully those paragraphs with “WARNING” or “CAUTION” symbols. They are important safety precautions to be aware of while transporting, installation, operating or examining the AC drive. Please follow these precautions to ensure your safety.

|  |  | WARNING | Personnel injury may be resulted by improper operation. |
| --- | --- | --- | --- |
|  | CAUTION |  | The AC Drive or mechanical system may be damaged by improper operation. |

WARNING

- Do not touch the PCB or components on the PCB right after turning off the power before the charging indicator went off. - Do not attempt to wire circuitry while power is on. Do not attempt to examine the components and signals on the PCB while the inverter operating. - Do not attempt to disassemble or modify internal circuitry, wiring, or components of the inverter. - The grounding terminal of the inverter must be grounded properly with 200V class type III standard. - This is a product of the restricted sales distribution class according to EN61800-3. In a domestic environment this product may cause radio interference in which case the user may be required to take adequate measures.

CAUTION

- Do not attempt to perform dielectric strength test to internal components of the inverter. There are sensitive semiconductor-devices vulnerable to high voltage in the inverter. - Do not connect the output terminals: T1 (U), T2 (V), and T3 (W) to AC power input - The CMOS IC on the primary PCB of the inverter is vulnerable to static electrical charges. Do not contact the primary PCB of the inverter.

# 2.	Examination before installation

Every inverter has been fully tested and examined before shipment. Please carry out the following examination procedures after unpacking your AC inverter.

- Check to see if the model number of the AC inverter matches the model number of the AC inverter that you ordered.

- Check to see whether any damage occurred to the AC inverter during shipment. Do not connect the AC inverter to the power supply if there is any sign of damage.

Report this to a regional sale representative if you find any abnormal condition as mentioned above.

Chapter 1: Safety Precaution

# 1. 	Precautions for operation

## Before turning ON power

CAUTION

Choose the appropriate power source with correct voltage settings for the input voltage specification of the AC inverter.

WARNING

Special care must be taken while wiring the primary circuitry panel. The L1 and L2 terminal must be connected to the input power source and must not be mistakenly connected to T1, T2 or T3 out put terminals. This may damage the inverter when the power is turned on.

CAUTION

- Do not attempt to transport the inverter by the front of the cover. Securely hold the inverter by the heat-sink mounting chassis to prevent the inverter from falling, this may cause personnel injury or damage to the inverter itself. - Install the inverter onto a firm metal base plate or another non-flammable type material. Do not install the inverter onto or nearby any flammable material. - An additional cooling fan may need to be installed if several inverters are installed into one control panel. The inside temperature inside an enclosed panel should be below 40 degrees to avoid overheating. - Turn off the power supply before proceeding to remove or perform any work on any panel. Carry out installation procedures according to instructions given in order to avoid a situation resulting in an operational malfunction. - Suitable for use on a circuit capable of delivering not more than 5000 RMS symmetrical amperes. 240 Volts maximum. - This product is not provided with over speed protection. - Only intended for use in a pollution degree 2 macro environment or equivalent

## When power is applied

WARNING

- Do not attempt to install or remove input or output connectors of inverter when the power supply is turned on. Otherwise, the inverter may be damaged due to the surge peak caused by the insertion or removal of power. - When momentary power loss is longer than 2 seconds (the large of horse power, the longer of time), the inverter does not have enough storage power to control the circuit; Therefore, when power is regenerated, the operation of the inverter is based on the setup of F_10 and the condition of external switch, this is considered to be「restart」in the following paragraphs. - When the momentary power loss is short, the inverter still has enough storage power to control the circuit; therefore, when power is regenerated, the inverter will automatically start operation again depends on the setup of F_23. When restart the inverter, the operation of the inverter is based on the setup of F_10 and the condition of external switch (FWD/REV button). Attention: the restart operation is irrelevant with F_23/F_24. - When F_10=0, the inverter will not start after restart. - When F_10=1 and the external switch (FWD/REV button) is OFF, the inverter will not start after restart. - When F_10=1 and the external switch (FWD/REV button) is ON, the inverter will start automatically after restart. Attention: Base on safety reason, please turn off the external switch (FWD/REV button) after power loss to avoid possible damage to the machine and the human body after sudden regeneration of power.

## Under Operation

WARNING

Do not use a separate device to switch ON or OFF motor during operation. Otherwise, the inverter may experience an over-current breakdown.

WARNING

- Do not remove the front cover of the inverter when the power is ON to avoid personnel injury caused by electrical shock. - When the automatic restart function is enabled, the motor and machinery will be restarted automatically.

CAUTION

- Do not touch the heat-sink base during operation. - The inverter can be easily operated from a low-speed to high-speed range. Please reconfirm the operating range of motor and the machinery you are controlling. - Do not examining the signals on the PCB of the inverter when it is under operation. - All inverters are properly adjusted and set before delivery.

CAUTION

Do not proceed with disassemble or examination procedure before ensuring that the power is off and the Power LED extinguished.

## When performing an examination or maintenance

CAUTION

Inverter environment should be within temp: –10 OC ~ +40 OC, humidity under 95% RH without condensing.

CAUTION

After the removal of shield sticker, the environment temperature should be within –10OC ~ +50OC and humidity under 95% RH without condensing. Besides, the inverter should be free from water dripping or metal dust.

# 2.	Precautions of operation environment

| Avoid any direct sunlight Keep away from corrosive gas or liquid Keep away from oil grease and gas oil |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Keep away from salty environments Keep away from rain or where dripping water may get into the inverter Avoid metal dust and dusty environments |  |  |  |  |  |  |  |  |
| Avoid massive vibration Avoid excessive direct heat Avoid where environmental temperatures are too high |  |  |  |  |  |  |  |  |
| Keep away from high electrical-magnetic waves or ultra-high waves. Keep away from radioactive matter Keep away from flammable material |  |  |  |  |  |  |  |  |

Chapter 2: Hardware Instructions and Installation

# 1.	Operational Environment

The installation site of the inverter is very important. It relates directly to the functionality and the life span of your inverter. Please carefully choose the installation site to meet the following requirements:

- Mount the unit vertically

- Environment temperature: -10OC ~ +40OC (without shield sticker: -10OC ~ +50OC)

- Avoid placing close to any heating equipment

- Avoid water dripping or humid environment

- Avoid direct sunlight

- Avoid oil or salty corrosive gas

- Avoid contacting corrosive liquid or gas

- Prevent foreign dusts, flocks, or metal scraps from entering interior

- Avoid electric-magnetic interference (soldering or power machinery)

- Avoid vibration, if vibration cannot be avoided, an anti-rattle mounting device should be installed to reduce vibration.

- If the inverter is installed in an enclosed control panel, please remove the shield sticker located at the top of the inverter. This will allow additional airflow and cooling.

External Fan Placement needs to be over the top of the inverter

Correct Alignment		Wrong Alignment	      Correct Alignment	     Wrong Alignment

- For proper Installation of the inverter you must place the front side of the inverter facing front and the top of the inverter in the up direction for better heat dissipation.

- Installation must be compliant to the following requirements.

Ventilation & Installation Direction

Front View

Note:  Maximum temperature in the enclosure 50 ℃

# 2.	Sample Model No. Identification

Inverter Model					MODEL: E2-201-M1F

Input Power Rating				I/P: AC 1PH 200 ~ 240V 50/60 Hz

Output Rating					O/P: AC 3PH 0 ~ 240V 1 Hp  4.2 Amps

E2  -      2               01      -         M                 1             F                N4

| Series |  | Power Voltage |  | Horse Power Rated |  | Model Type |  | Power Supply |  | Filter Option |  | Enclosure Type |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

1 : 110V

2 : 220V

4 : 440V

P2 : 0.25 Hp

P5 : 0.5 Hp

01 : 1 Hp

02 : 2 Hp

03 : 3 Hp

M : CPU Version

V1.6

H : CPU Version

V1.9 or above

1 : Single

Phase

3 : Three

Phase

Blank :

Single or

Three Phase

F :

with filter

Blank :

without filter

N4S :

meet IP65/NEMA4

Standard with

Switch

N4 :

meet IP65/NEMA4

Standard without

Switch

Blank : IP20

3.Specification:

Basic specification:

| Model : E2- |  | 1P2-H1x | 1P5-H1x | 101 |
| --- | --- | --- | --- | --- |
| Suitable Motor Power Rating (KW) |  | 0.2 | 0.4 | 0.75 |
| Rated | Motor (HP) | 0.25 | 0.5 | 1 |
|  | Output Current (A) | 1.4 | 2.3 | 4.2 |
|  | Capacity (KVA) | 0.53 | 0.88 | 1.6 |
|  | Weight (Kg ) | 0.7 | 0.72 | 0.8 |
| Input Voltage Max. |  | Single phase 100-120V (+10%, -15%), 50 / 60Hz (+/-5%) |  |  |
| Output Voltage Max. |  | Three phases 200-240V (Proportional to input voltage) |  |  |
| Dimension W*H*D (mm) |  | 72*132*118 |  |  |
| EMC Specification |  | Without Filter |  |  |

| Model: E2- |  | 2P2-x1xx | 2P5-x1xx | 201-x1xx | 202-Hxxx | 203-Hxxx |
| --- | --- | --- | --- | --- | --- | --- |
| Suitable Motor Power Rating (KW) |  | 0.2 | 0.4 | 0.75 | 1.5 | 2.2 |
| Rated | Motor (HP) | 0.25 | 0.5 | 1 | 2 | 3 |
|  | Output Current (A) | 1.4 | 2.3 | 4.2 | 7.5 | 10.5 |
|  | Capacity (KVA) | 0.53 | 0.88 | 1.6 | 2.9 | 4.0 |
|  | Weight (Kg) | 0.76 | 0.77 | 0.8 | 1.66 | 1.76 |
| Input Voltage Max. |  | Single phase 200-240V (+10%, -15%), 50 / 60Hz (+/-5%) |  |  | Single/Three phases 200- 240V(+10%, -15%), 50 / 60Hz (+/-5%) |  |
| Output Voltage Max. |  | Three phases 200-240V (Proportional to input voltage) |  |  |  |  |
| Dimension W*H*D (mm) |  | 72*132*118 |  |  | 118*143*172 |  |
| EMC Specification |  | Class A (Single Phase Filter built in) |  |  |  |  |

| Model : E2- |  | 401-H3xx | 402-H3xx | 403-H3xx |
| --- | --- | --- | --- | --- |
| Suitable Motor Power Rating (KW) |  | 0.75 | 1.5 | 2.2 |
| Rated | Motor (HP) | 1 | 2 | 3 |
|  | Output Current (A) | 2.3 | 3.8 | 5.2 |
|  | Capacity (KVA) | 1.7 | 2.9 | 4.0 |
|  | Weight (Kg ) | 1.6 | 1.62 | 1.68 |
| Input Voltage Max. |  | Three phases 380-480V (+10%, -15%), 50 / 60Hz (+/-5%) |  |  |
| Output Voltage Max. |  | Three phases 380-480V (Proportional to input voltage) |  |  |
| Dimension W*H*D (mm) |  | 118*143*172 |  |  |
| EMC Specification |  | Class A (Three Phases Filter built in) |  |  |

Functional specification:

| Item |  |  | Specification |
| --- | --- | --- | --- |
| Input Signal Type |  |  | PNP type (SOURCE) input (External 24VDC Input is allowed) |
| Control Method |  |  | Sinusoidal wave PWM control |
| Freq. Control | Freq. Range |  | 1~200 Hz*1 |
|  | Resolution Setting |  | Digital: 0.1 Hz (1 ~ 99.9 Hz); 1 Hz (100 ~ 200 Hz) Analog: 1Hz/ 60 Hz |
|  | Keyboard Setting |  | Directly setup by ▲▼ buttons. |
|  | External Signal Setting |  | 0~10V, 4 ~ 20mA, 0 ~ 20mA |
|  | Other function |  | Frequency upper and lower limit |
| General Control | Carrier frequency |  | 4~16KHz*2 |
|  | Accelerate/Decelerate time |  | 0.1~ 999 Sec |
|  | V/F Pattern |  | 6 Patterns |
|  | Torque control |  | Torque boost level adjustable (manual torque boost) |
|  | Multi-Functional input |  | 2 point, to be used as multi-speed 1(Sp.1) / multi-speed 2(Sp.2) *1/ Jog / External emergency stop / External bb / Reset |
|  | Multi-Functional output |  | 1a Relay terminal, to be setup as Fault / Running / Frequency. |
|  | Braking Torque |  | 1P2~101/2P2~201:About 20% 202/203/401/402/403: 20%~100%, built-in braking transistor |
|  | Other function |  | Decelerate or free run stop, Auto reset, DC braking frequency / Voltage / Time can be setup by constants. |
| Display |  |  | Three digital LED display frequency / inverter parameter / fault record / program version. |
| Operating temperature |  |  | -10 ~ +40OC (without shield sticker: -10OC ~ +50OC) |
| Humidity |  |  | 0~95% RH non-condensing. |
| Vibration |  |  | Under 1 G (9.8 m/s2) |
| EMC specification |  |  | EN50081-1, EN50081-2, EN50082-2, EN61800-3+A11,EN50178 |
| UL |  |  | UL508C |
| Protection Function |  | Overload protection | 150% for 1 min. |
|  |  | Over-voltage | DC voltage > 410V(100/200 series); DC voltage > 800V(400 series) |
|  |  | Under voltage | DC voltage < 200V(100/200 series); DC voltage < 400V(400 series) |
|  |  | Momentary Power-loss | 0 ~ 2 sec: The inverter can be restarted using speed search feature. |
|  |  | Stall Prevention | During Acceleration / Deceleration/ Constant speed |
|  |  | Output Short-circuit | Electronic circuitry protection |
|  |  | Grounding fault | Electronic circuitry protection |
|  |  | Other function | Heat sink overheat protection, Current limit |
| Installation |  |  | Mounting screw or DIN rail (Option). |

Note: *1: New function for CPU version v1.9 and above.

*2:  Carrier frequency range: CPU version v1.6 is 4~8kHz.

CPU version v1.9 and above are 4~16kHz.

## Suitable optional and Wiring Specification

Molded-Case Circuit Breaker / Magnetic Contact

- Warrantee does not apply to damage caused by the following situations:

- Damage to the inverter caused by the lack of appropriate molded-case circuit breaker or when a circuit breaker with too large of capacity is installed between the power supply and the inverter.

- Damage to the inverter caused by the magnetic contact, phase advancing capacitor, or surge-protector installed between the inverter and the motor.

| Model Type | 1P2/1P5/2P2/2P5 | 101/201/202 | 203 | 401/402/403 |
| --- | --- | --- | --- | --- |
| Molded-case circuit breaker | 15A | 20A | 30A | 15A |
| T3 T1 T2 L1 Primary Circuit Terminal (TM1) L2 | Wire dimension (#14AWG) 2.0mm2 Terminal screw M3 | Wire dimension (#14AWG) 2.0m m2 Terminal screw M3/M4 | Wire dimension 3.5mm2 Terminal screw M4 | Wire dimension 3.5mm2 Terminal screw M4 |
| Signal Terminal (TM2) 1~11 | Wire dimension 0.75mm2 (#18 AWG), Terminal screw M3 |  |  |  |

Use copper conductors only size field wiring based on 80 degrees C wire only.

- Please utilize three-phase squirrel-cage induction motor with appropriate capacity.

- If the inverter is used to drive more than one motor, the total capacity must be smaller than the capacity of the inverter. Additional thermal overload relays must be installed in front of each motor. Use the Fn_18 at 1.0 times of the rated value specified on the motor nameplate at 50Hz, 1.1 times of the rated value specified on the motor nameplate at 60Hz.

- Do not install phase advancing capacitors, LC, or RC component between the inverter and the motor.

Application and precautions of Peripherals

From the Power Source: - Apply the power source at the correct rated voltage to prevent from damaging the inverter. - A Power Disconnect or Circuit breaker must be installed between the AC power supply and the inverter. Molded-case circuit breaker: - Utilize an appropriate circuit breaker that’s suitable for the rated voltage and current ratings of the inverter to switch ON/OFF the power supply to the inverter and as additional protection for the inverter. - Do not operate the circuit breaker to switch ON or OFF the inverter. The circuit breaker should be used only to supply input power and should not be used for operational sequence. Leakage circuit breaker: - An earth leakage circuit breaker should be added to prevent false operation cause by leakage current and to ensure personnel safety. Magnetic Contact: - The Magnetic Contact can be omitted at ordinary operation. To utilize external control, automatic restart, or breaking controller the magnetic contact must be added at the primary side. - Do not operate the magnetic contact to switch ON or OFF the inverter. Power improvement AC Reactor: - If large capacity power source is applied (over 600KVA), additional AC reactor may be added to improve power factor. Inverter: - Power supply input terminals L1 and L2 are not differentiated on phase sequence. They can be arbitrarily connected. Their connection may be interchanged. - Output terminal T1, T2, and T3 should be connected to the U, V, and W terminals of the motor respectively. If motor turns in opposite direction of the inverter command, simply exchanging two of the three wire connections will correct this problem. - Output terminal T1, T2, and T3 must not be connected to power source to prevent from damaging the inverter. - Grounding terminal properly ground the grounding terminal in compliance to 200V class type three grounding. (The 400V class type is special grounding.)

External wiring should be carried out in accordance with following requirement. Check and reassure the wiring is correct after the wiring is complete.

(Do not utilize the control circuitry buzzer to check the wiring.)

EMI connections:

It is very important that the connections between the inverter, the shielded motor cable, and the EMI filters are tested as follows.

- Use a metal grounding plate and place the frequency inverter and the EMI filter on the plate.

- Use a shielded motor cable with 4 connectors (U, V, W, & Earth), don’t use the shielding as safety earth (shield is high frequency earth)

- Remove any paint around the two metal coupling nut holes. So that the metal coupling nuts (and the shielding) make contact with the frequency inverter and the motor.

- Don't solder a conductor to the shielding.

- Use a metal clamp to connect the shielding from the motor cable with the metal grounding plate. Now there is a perfect high frequency earth connection between frequency inverter, grounding plate and EMI filter.

- Keep the distance between the frequency inverter and EMI filter as short as possible (< 30cm) if longer use a shielded cable with a metal coupling nut and a metal clamp to connect the shielded cable to the frequency inverter and metal grounding plate.

- The only earth connection between the LISN and the test plate should be via the EMI filter.

- Use a motor which equals the power rating or below of the inverter rating.

- Install a noise filter for inverter onto the output side of the primary circuitry can suppress conducting noise.

Class B:

Class A:

When the distance between the inverter and motor is longer than 100 meters, cable wire should be carefully chosen to reduce the wiring resistance below 3% and the voltage drop (V) = √3 x Wire resistance (Ω/km) x wire length (m) x current x 10-3

(B)	Control circuitry wiring must be separated terminated and away from the primary power circuitry and other high-voltage or large-current power lines to avoid noise interference.

- To reduce the noise interference and avoid possible operational problems, shielded twisted pair cable should be used to wire the control circuitry. Please refer to following diagram. Connect the shielding wire onto the grounding terminal.  Only connect one end of the shield.

Wiring distance must be under 50m.

Shielding

Glove

To control machine

Do not connect the shielding wire at this end

To Inverter terminal

Connect to system grounding terminal

Wrapped with insulating tape

Connect Shield

(C)	The grounding terminal of the inverter must be correctly grounded in compliance with 200V class type three grounding.

- Grounding wire should be wired in accordance to electrical equipment (AWG) with the length of the grounding wire as short as possible.

- The grounding wire of the inverter must not be grounded together with other large current loads (such as soldering machines or large current motors). They should be grounded separately.

- Grounding circuitry must not be formed when grounding several inverters together.

(a) good 	    	         (b) good				              (c) not good

(D)	Wire specification, apply appropriate wire with correct diameter for primary power circuitry and control circuitry in accordance with electricity regulations.

#### Wiring Diagram

Wire Terminations to the Inverter must be made with either UL listed field wiring lugs or UL listed crimp

type ring terminals.

Note: Only for 202/203/401/402/403.

- (External 24V supply)